Conveyor Motor Control - How the Ladder Logic Works (Rungs A –> D)

What this program is meant to do

This ladder logic controls a conveyor motor with:

- Start / Stop pushbuttons

- Emergency stop override (E-Stop)

- A seal-in latch (so the motor keeps running after you release Start)

- An optional AutoStop timer (stops the conveyor automatically after 30 seconds)

- No auto-restart after power loss (because the latch is non-retentive)

Signals / Tags used

Inputs

- Start_PB: Start button (momentary). TRUE when pressed.

- Stop_PB: Stop button. In this design it’s normalized: TRUE = healthy/not pressed (typical NC wiring).

- EStop_OK: Emergency stop healthy. Also normalized: TRUE = healthy (E-Stop not pressed).

- AutoStop_Enabled: Enables the 30s auto stop feature.

Internal bits

- Permissive_OK: “All safety conditions are good, we are allowed to run.”

- Run_Latch: Memory bit that holds the run command (seal-in).

Timer

- T_AutoStop (TON, 30s): Runs while the conveyor is running (and AutoStop_Enabled is TRUE).

  - T_AutoStop.Q becomes TRUE when 30 seconds has elapsed.

Output

- Motor_Run: Output coil that drives the motor starter/contactor.

Key assumption (important for safety logic)

This program assumes Stop_PB and EStop_OK are normalized:

- TRUE = healthy (circuit closed / not pressed)

- FALSE = not healthy (button pressed / circuit open)

This matches typical real-world NC safety wiring (fail-safe: a broken wire looks like a stop).

Rung-by-rung explanation

Rung A - Master Permissive (Safety Gate)

What it does:
This rung creates a single “permission to run” signal:

Permissive_OK = EStop_OK AND Stop_PB

So:

- If E-Stop is pressed -> EStop_OK = FALSE -> Permissive_OK = FALSE

- If Stop is pressed -> Stop_PB = FALSE -> Permissive_OK = FALSE

- Only when both are healthy does Permissive_OK become TRUE

Think of this as the main safety gate that everything else must pass through.

Rung B - Seal-in Latch with AutoStop Cutout (Platform-agnostic)

What it does:
This rung “remembers” the Start button press and keeps the conveyor running:

Run_Latch = Permissive_OK AND (Start_PB OR Run_Latch) AND NOT T_AutoStop.Q

Breakdown:

- Permissive_OK must be TRUE (safety is OK)

- (Start_PB OR Run_Latch) is the seal-in logic:

  - Start gives an initial TRUE

  - Then Run_Latch keeps itself TRUE after you release Start

- NOT T_AutoStop.Q is the auto-stop cutout:

  - Once the timer is “done” (Q = TRUE), this becomes FALSE, and the latch drops.

Why this design is strong:

- It doesn’t rely on special “reset coils” or scan-order quirks.

- It’s easy to reason about and works on basically any PLC ladder platform.

Rung C - AutoStop Timer (TON 30s)

What it does:
This rung runs the timer only while:

- the conveyor is latched on, and

- auto-stop is enabled

T_AutoStop.IN = Run_Latch AND AutoStop_Enabled
PT = 30 seconds

So:

- If AutoStop_Enabled is FALSE, the timer never runs.

- If the motor stops (Run_Latch goes FALSE), the timer resets (as TON timers do).

After 30 seconds of continuous running, T_AutoStop.Q becomes TRUE.

That TRUE is then used in Rung B to cut the latch.

Rung D - Motor Output (Final Gate)

What it does:
This rung drives the real motor output:

Motor_Run = Run_Latch AND Permissive_OK

So even if Run_Latch was somehow TRUE, the motor still cannot run unless Permissive_OK is TRUE.

This is a good safety habit: safety conditions should directly gate the final output.

What happens in real life (quick scenarios)

Normal start

- E-Stop healthy, Stop not pressed -> Permissive_OK = TRUE

- Press Start -> Run_Latch turns TRUE

- Release Start -> Run_Latch stays TRUE (seal-in)

- Motor runs because Motor_Run = TRUE

Press Stop

- Stop makes Stop_PB = FALSE -> Permissive_OK = FALSE

- That immediately forces:

  - Run_Latch to drop (because Permissive_OK is required in Rung B)

  - Motor_Run to drop (because Permissive_OK is required in Rung D)

Press E-Stop

Same idea as Stop, except it’s the emergency channel:

- EStop_OK = FALSE -> motor drops immediately

AutoStop enabled

- Timer runs while running

- After 30 seconds: T_AutoStop.Q = TRUE

- That makes NOT T_AutoStop.Q = FALSE -> latch drops -> motor stops

Power loss / PLC restart

Because Run_Latch is non-retentive, it does not come back TRUE after power returns.
So the conveyor will not restart automatically, the operator must press Start again.

Why this (and common mistakes avoided)

- Safety inputs are treated as permissions (healthy = TRUE)

- Motor output is always gated by safety (Permissive_OK)

- Seal-in latch is implemented clearly and safely

- AutoStop is optional, and implemented in a platform-agnostic way (no set/reset dominance issues)

- No auto-restart after power loss